Market:

Power

Challenge:

External crack to a 78-in circulating water pump expansion joint caused extensive leakage and forced the power station to shut down.

Engineered Solution:

The solution utilized the HydraTite® seal consisting of three two-piece 304 stainless steel bands, a double wide EPDM seal, and a 16 gauge stainless steel backing plate to provide an internal slip joint repair.

Scope:

The crew and all materials entered through an opening provided by the client and were able to complete the HydraTite® system installation safely and within one day.

Solution:

Once the HydraTite® internal seal was installed, the leak was isolated and the circulation system was operational. This saved the power company extended downtime.

HydraTech Engineered Products, LLC

10448 Chester Road, Cincinnati Ohio 45215      Phone: (513) 827-9168      Fax: (513) 827-9171

https://hydratechllc.com